## Sheet1
(Admin. Block) Appendix- H
LT Electrification
Item No | Unit | Specification of Items | Rate in rupees | Qty | Amount in Rupess
1 |  | Supply and wiring points according to IS 732-1989 through the existing conduit with 1.00 sq mmFR PVC insulated stranded single core copper conductor cable 650V grade, 1.5sqmm green coloured FR wire for earth, required qty of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white) etc. up to and including 6 A modular type ROHS compliant SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required.
a | Each | Single control light point with 6A, 3 plate ceiling rose | 676 | 190 | 128440
b | Each | Twin control light point with 6A, 3 plate ceiling rose | 1014 | 2 | 2028
c | Each | Single control light point without ceiling rose | 657 | 37 | 24309
d | Each | Twin control light point without ceiling rose | UR
2 | Each | Single control ceiling fan point with 6 A, 3 plate ceiling rose & with socket size stepped electronic regulator. | 1309 | 97 | 126973
3 | Each | Call bell point with piano type 6 A bell push at one end and 6 A, 3 plate ceiling rose at other end | 714 | 3 | 2142
4 | Each | Combined plug point with 6 A, 5 pin plug socket controlled by 6 A switch in the same switch board as that of light points. | 338 | 21 | 7098
5 | Each | Supply 3no 6A socket controlled by 1no 10A control switch modular type in company made box and front plate | 1010 | 46 | 46460
6 | Each | Supply and installation of RJ 45 computer jack in suitable plastic box with front plate (modular) | 385 | 46 | 17710
7 | Each | Supply and fixing RJ 11 twin telephone sockets | 405 | 8 | 3240
8 | Each | Supply and wiring 6A 3 pin sockets controlled by 6A SP switch in independent position. | 644 | 2 | 1288
9 | Each | Supply and installation of suitable size MS rod type fan clamp as per IS 732 as required. | 124 | 20 | 2480
10 | Each | Supply and installation of suitable size MS belt type fan clamp fabricated from MS flat (2 pieces) as per IS 732 as required. | 182 | 20 | 3640
11 | Each | Conveyance installation testing and commissioning ceiling fan of all sizes using standard accessories including step regulator, wiring the down rod with 16/0.20mm PVC insulated and PVC sheathed 650/1100V grade 3 core round copper conductor flex wire or extending the original wiring etc. as required. | 100 | 90 | 9000
12 | Each | Conveyance installation testing and commissioning ceiling fan of all sizes on suitable size heavy guage 300mm long GI/ WI pipe including cutting, drilling, and painting the rod, wiring the down rod with 16/0.20mm PVC insulated and PVC sheathed 650/1100V grade 3 core round copper conductor flex wire or extending the original wiring etc. as required. | 146 | 7 | 1022
13 | mtr | Supply and providing every additional length of down rod of suitable size heavy gauge GI / WI pipe with 16/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming in relevant ISS or with original wiring extended including painting as required. | 115 | 2 | 230
14 | Each | Conveyance, installation, testing and commissioning of pre-wired fluorescent light fittings with all accessories and fluorescent lamps of all types directly on wall and giving connections with 16/0.20 mm 3 core PVC insulated and sheathed round copper conductor flex wire or extending the original wiring and giving connections as required | 138 | 137 | 18906
15 | Each | Conveyance, installation, testing and commissioning of pre-wired fluorescent fittings of all types complete with all accessories and fluorescent lamps etc. including supplying and fixing ball and socket arrangements on T.W round block, suspension down rod of 19 mm dia MS conduit up to 2x30cm length including painting and wiring the down rod with 16/0.20mm 3 core round copper conductor flex wire conforming to relevant ISS or extending the original wiring and giving connections etc. as required. | 371 | 25 | 9275
16 | mtr | Supplying and providing extra H.G conduit down rod of 19 mm dia 2 x 1.00 m long with 16/0.20 mm 3 core copper conductor flex wire conforming to relevant ISS or with the extended original wiring and giving connection etc. as required. | 198 | 10 | 1980
17 |  | Supply, conveyance, installation, testing and commissioning of pre-wired fluorescent fitting of the following types complete with all accessories and fluorescent lamps etc on suitable GI pipe bend to shape, painted and giving connections with required length of 16/0.20mm 3 core copper conductor flex wire conforming to relevant ISS or extending the original wiring and giving connection etc. as required. |  |  | 0
a | Each | S&F 2x18W Fluorescent street light fitting with aluminium housing, stove enameled CRCA sheet steel reflector cover, acrylic cover complete with lamp holder, APF electronic ballast suitable for continuous operation with THD <10%, power factor >0.98, RoHS compliant,high lumen tube, duly wired up for use on 230 V AC supply with lamps. | 2521 | 12 | 30252
18 | Each | Conveyance, installation, testing and commissioning of exhaust fans of size up to 450 mm in the existing opening, fixing necessary bolt and nuts, making good the damages etc. as required including giving connections with required length of 24/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming to relevant ISS. | 318 | 9 | 2862
19 | Each | Supply and fixing angle / straight brass lined skirt type, bakelite batten holder without shade and giving connection etc as required | 63 | 37 | 2331
20 | Each | Supply and fixing 11W CFL lamp in the existing holder | 156 | 46 | 7176
21 | Each | Supply and fixing cast aluminium stove enameled bulk head fitting with deep drawn anodised aluminium body, epoxy powder coated, heat resistant prismatic glass cover suitable for 9 W CFL to wall / ceiling including giving connections with required length of 16/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming to relevant ISS or extending the original wiring and making good the surface as required. | 601 | 10 | 6010
22 | Each | Supply and fixing 6/16A shuttered socket with16A control switch modular type in company made box and front plate.(Group B) | 665 | 10 | 6650
23 | Each | Supply and fixing modular switch and accessories in 4 module box with front plate with 20A starter, 20A socket and 20A plug top. | 854 | 1 | 854
24 | Each | Supply and fixing modular switch and accessories in 4 module box with front plate with 25A starter, 25A socket and 25A plug top. | 854 | 6 | 5124
25 |  | Supply and laying medium gauge PVC conduit conforming to IS 9537/1983 Part III n roof slab, jointing the pipes with PVC solvent cement, tying & fixing the conduit firmly with the re-inforcement etc. as required. |  |  | 0
a | mtr | 20 mm | 41 | 2300 | 94300
b | mtr | 25 mm | 49 | 700 | 34300
26 |  | Supply and fixing the following deep PVC accessories conforming to IS 3419/1988 along with the PVC conduits laid in concrete |  |  | 0
a | Each | 20 mm 1 way deep junction box | 50 | 130 | 6500
b | Each | 20 mm two way through junction box | 51 | 80 | 4080
c | Each | 20 mm 3 way angle junction box | 52 | 60 | 3120
d | Each | 20 mm 4 way angle junction box | 55 | 100 | 5500
e | Each | 25 mm 1 way deep junction box | 53 | 5 | 265
f | Each | 25 mm two way through junction box | 56 | 5 | 280
g | Each | 25 mm 3 way angle junction box | 58 | 5 | 290
h | Each | 25 mm 4 way angle junction box | 61 | 5 | 305
27 |  | Supply and fixing the following sizes of medium guage PVC Conduit conforming to IS 9537 / 1983 part III along with all required accessories in recess including cutting the wall and making good the damages etc as required. |  |  | 0
a | mtr | 20mm | 124 | 200 | 24800
b | mtr | 25mm | 136 | 100 | 13600
28 |  | Supply and drawing 650/1100 V grade PVC insulated stranded single core copper conductor cables conforming to IS 694 part I 1990 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  |  | 0
a | mtr | 1.5sq mm 3 run( R/Y/B/Black/Green) | 77 | 1000 | 77000
b | mtr | 1.5sq mm single run( green) | 45 | 110 | 4950
c | mtr | 2.5sq mm 2 run | 81 | 110 | 8910
d | mtr | 4sq mm 2 run | 106 | 110 | 11660
e | mtr | 4sq mm 4 run | 184 | 70 | 12880
f | mtr | 6sq mm 4 run | 260 | 50 | 13000
29 | mtr | Supply and drawing No.14 SWG copper along with 4sq.mm mains | 26 | 110 | 2860
30 | mtr | Supply and drawing No.10 SWG copper along wiring | 62 | 250 | 15500
31 | nos | Supply and providing superior quality copper earth socket suitable for No.14 SWG copper and Crimping | 18 | 14 | 252
32 | nos | -Do- No.10 -Do - | 19 | 36 | 684
33 | mtr | Supplying and clamping 25 x 3 mm tinned Copper strip on wall | UR
34 |  | Supply, laying and clamping of 1 no.XLPE insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  |  | 0
a | mtr | 4x16 sq mm | 231 | 25 | 5775
b | mtr | 4x10 sq mm | 197 | 15 | 2955
35 |  | Supplying siemens / tropodur type nickel plated single compression brass cable gland for PVC insulated and PVC sheathed armoured aluminium/ copper conductor cable 1.1 KV grade, and making end termination suitable for 2/ 3/ 3½/ 4 core cable of the following sizes as required. |  |  | 0
a | nos | 16 sq mm | 319 | 4 | 1276
b | nos | 10 sq mm | 271 | 2 | 542
36 |  | Supplying and providing earth clamps for siemens/ tropodur type cable glands of suitable length and other dimensions noted along with each size of glands for the following sizes of cables as required. |  |  | 0
a | nos | 16 sq mm | 18 | 4 | 72
b | nos | 10 sq mm | 18 | 2 | 36
37 |  | Supply of superior quality aluminium tubular cable socket and making core termination of cables of the following sizes including crimping etc. as required. |  |  | 0
a | nos | 16 sq mm | 13.7 | 16 | 219.2
b | nos | 10 sq mm | 12.7 | 8 | 101.6
38 |  | Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  |  | 0
0
a | nos | DP enclosure for independent mounting of MCB | 486 | 2 | 972
b | nos | 4P enclosure for independent mounting of MCB | 604 | 2 | 1208
c | nos | 6 W 1 phase double cover | 1456 | 1 | 1456
39 | nos | 3ph 4W double cover TPN vertical DB with provision for fixing 4pole MCB/Isolator/RCCB as incomer and SP/TP MCB as outgoings IP54 | 9082 | 2 | 18164
40 | nos | 3ph 6W double cover TPN DB with provision for fixing 4pole MCB/Isolator/RCCB as incomer and SP/TP MCB as outgoings IP54 | 7700 | 2 | 15400
41 | nos | 3ph 4W double cover TPN DB with provision for fixing 4pole MCB/Isolator/RCCB as incomer and SP/TP MCB as outgoings IP54 | 6434 | 4 | 25736
42 |  | Supply and installation of the following accessories suitable for 50 Hz , AC supply conforming to IS 8828-1995/ IEC 60898 of the following current ratings in the existing enclosure and giving connections as required |  |  | 0
a | nos | S&F 63A 4P Minibreak Isolator | 752 | 3 | 2256
b | nos | S&F 32A 4P Minibreak Isolator | 667 | 6 | 4002
c | nos | S&F 25A 2P Minibreak Isolator | 342 | 3 | 1026
d | nos | Supply and fixing 40A 100mA FP RCCB | 2881 | 3 | 8643
e | nos | Supply and fixing 25A 30mA FP RCCB | 2744 | 4 | 10976
f | nos | Supplying and fixing 32A 4P MCB 10kA | 1180 | 1 | 1180
g | nos | Supplying and fixing 32A TP MCB 10kA | 908 | 1 | 908
h | nos | Supplying and fixing 25A TP MCB 10kA | 919 | 3 | 2757
i | nos | Supplying and fixing 25A SP MCB 10kA | 219 | 13 | 2847
j | nos | Supplying and fixing 16A SP MCB 10kA | 219 | 11 | 2409
k | nos | Supplying and fixing 10A SP MCB 10kA | 219 | 36 | 7884
l | nos | Supplying and fixing 6A SP MCB 10kA | 219 | 36 | 7884
m | nos | Supply and istallation of cable box for 3 ph 4W DB | 924 | 3 | 2772
43 |  | Cost of fittings |  |  | 0
44 |  | Cost of Fluorescent tube light fitting with lamp holder, APF electronic ballast suitable for continuous operation with THD <10%, power factor >0.98, RoHS compliant,high lumen tube, duly wired up for use on 230 V AC supply . The fittings shall be made from CRCA MS sheet of minimum thickness 0.50 mm nominal thickness inside & outside. |  |  | 0
45 | nos | Suitable for single 28W T5 lamp | 1322 | 60 | 79320
46 | nos | Suitable for Twin 28W T5 lamp | 1937 | 102 | 197574
47 | nos | Supply of 1200mm ceiling fan( 5 star rated) of the following sizes using standard accessories excluding resistance type regulator, wiring the down rod with 16/0.20mm PVC insulated and PVC sheathed 650/1100V grade 3 core round copper conductor flex wire or with extended original wiring etc. as required. | 1853 | 97 | 179741
48 |  | Supply, conveyance, installation, testing and commissioning of the following sizes of exhaust fans in the existing opening, fixing necessary bolt and nuts, making good the damages etc. as required including giving connections with required length of 24/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming to relevant ISS. |  |  | 0
49 | nos | 300/ 305 mm, single phase light duty exhaust fan in metal frame (Group B) | 1828 | 8 | 14624
50 | nos | 450 mm, single phase, heavy duty, 1400 rpm exhaust fan in metal frame | 4157 | 1 | 4157
51 | nos | Supply and providing plate earthing as per IS 3043 with 1200x1200x12 mm GI/CI earth plate, 50 mm GI watering pipe fixed to the earth plate with 25 x 3mm GI clamps, GI funnel with weld mesh, filling required quantity of charcoal including construction of inspection chamber with a bed concrete of 1:4:8 PCC using 40 mm broken stone (10 cm thick), brick work in cement mortar 1:6, plastering the surface of brick masonry and the exposed surface of PCC bed with cement mortar 1:4, 12 mm thick, (the finished inside dimension shall be 450 x 450 x 450 mm) but excluding test joint, earth continuity conductor to the plate, and covering at the top. (in ordinary soil) | 10652 | 2 | 21304
52 |  | Supply and providing test joint for the earthing system using 2 Nos of the following sizes of strips including cutting and bending to shape, drilling necessary holes and fixed to the watering pipe etc as required. |  |  | 0
53 | nos | 2x40x3mm GI strip | 215 | 2 | 430
54 | nos | Supply and providing the following sizes of cast iron gully trap with covering at the top of the inspection chamber of earth pit as required |  |  | 0
55 | nos | 450x450x10mm | 929 | 2 | 1858
56 | mts | Supplying and connecting 25x6 GI strip from test joint to plate | 242 | 5 | 1210
57 | kg | Supplying and installation including all manner of supports/ suspenders, anchor bolts etc for cable trays made out of suitable size channel sections, slotted angles, flats, MS plates etc as required including painting with 2 coats of synthetic enamel paint over a coat of zinc chromate primer, making good the damages, colour washing etc as required. | 110 | 50 | 5500
58 | kg | Supplying and installation of supports, anchor bolts etc made out of suitable size single section MS angle, flats etc as required including painting with 2 coats of synthetic enamel paint | UR
|  |  | Total |  | 1437690.8
( Rupees Fourteen Lakh thirty seven thousand six hundred and ninety one only )
]
2875381.6