## Sheet1
Appendix - F
HT INSTALLATION
Item No | Qty | Unit of Measurement | Specification of Items | Unit Rate | Total
USS
1 | 1 | No | Supply installation, testing and commissioning of indoor unitized substation consisting of 1 no. 11KV 350MVA 630A 3Ph HT load break switch with suitable HRC fuses , with incoming through 11KV 3core 150sq.mm XLPE cable ,shunt trip earth switch fused with mechanism , fuse trip mechanism and 1 no. cast resin dry type 400KVA 11KV/433 V , 3 phase AN cooled, vector DYN-11 cast resin transformer with Off circuit tapings of +5% to -7.5% in steps of 2.5, changeable by tap links provided, with LV cable box suitable for 2 runs of 3.5 x 400SQMM PVC cable and HV terminals connected to 11KV seal off bushings to the transformer. (Supply by client) | 850000 | 850000
1.1 | 1 | No | Labour for mechanical erection of transformer and giving primary and secondary connections | 15000 | 15000
2 | 1 | No | Supply and installation of HT TOD Meter in existing enclosure and giving connectionsas per standards approved by KSEB including testing. | 35000 | 35000
3 | 30 | Mts | Supply, and laying of 11 kV XLPE 3 core, armoured, aluminium cable of 300 sq: mm size of approved make in existing masonry open duct as required neatly clamped on supports. | 2735 | 82050
3.1 | 10 | Mts | do- Clamped using 20x3mm MS Flat spacing not exceeding 60cm | 2799 | 27990
4 | 150 | Mts | Supply, and laying of 11 kV XLPE 3 core, armoured, aluminium cable of 150 sq: mm size of approved make in existing masonry open duct as required neatly clamped on supports. | 1684 | 252600
4.1 | 10 | Mts | do- Clamped using 20x3mm MS Flat spacing not exceeding 60cm | 1768 | 17680
5 | 1 | No | Supply and making dry, push on type outdoor end termination for 11kV, 3 core, 300 sqmm XLPE armoured aluminium cable including cable sockets, tapes, earthing, jointing, crimping etc complete | 11975 | 11975
6 | 1 | No | Supply and making dry, push on type indoor end termination for 11kV, 3 core, 300 sqmm XLPE armoured aluminium cable including cable sockets, tapes, earthing, jointing, crimping etc complete | 10748 | 10748
7 | 2 | No | Supply and making dry, push on type indoor end termination for 11kV, 3 core, 150 sqmm XLPE armoured aluminium cable including cable sockets, tapes, earthing, jointing, crimping etc complete | 8769 | 17538
8 | 20 | mts | Supply and laying 1 run of 3.5 x 400sq mm PVC insulated and PVC sheathed armoured power cable of best conductivity Aluminium, 1.1KV grade conforming to IS 1554 partly clamped in existing buit in trench as required | 1994 | 39880
9 | 4 | nos | Supply and providing end and core termination for 3.5 x 400sqmm cable including cost of gland cable socket, earth etc including crimping etc | 1487 | 5948
10 | 1 | No | Supply and installation of one number neutral CT 120/5A 15 VA class 5P10 weather proof metal enclosure for CDG11 low set earth fault relay and giving connection as required | 3500 | 3500
10.1 | 1 | No | do- earth fault relay CDG 11 and giving connection etc as required | 10500 | 10500
11 | 3 | nos | Supply and providing pipe earthing as per IS 3043 with 2.5 m 38/40mm GI pipe | 2500 | 7500
12 | 6 | nos | Supply and providing plate earthing as per IS 3043 with 1200x1200mmx12.3mm CI/GI Plate with 50mm dia GI watering pipe fixed to earth plate with 25x3mm GI clamps, GI funnel with welded mesh filling the pit with the required quantity of charcoal and sand providing 450x450x450mm inspection chamber with brick work in cement mortar 1:6 plastering the surface of brick masonry, etc complete as required. | 10652 | 63912
13 | 6 | nos | Supply and Providing cast iron gully trap with covering at top of the inspection chamber(450x450x10mm). | 929 | 5574
14 | 6 | nos | Supply and providing test joint for the earthing system using two numbers of 50x3mm GI strip including cutting and bending to shape, drilling necessary holes and fixed to watering pipes. | 248 | 1488
15 | 30 | Mts | Supply and providing earth lead from test joint to earth plate using 50x6mm GI strip | 275 | 8250
16 | 60 | mts | Supplying and providing 25 x 6mm bare Cu strip for connection of earth electrodes(For neutral earthing of transformer) | 957 | 57420
17 | 40 | mts | Supplying and providing 25 x 3mm Cu strip for interconnection of earth electrodes(For neutral earthing of generator) | 483 | 19320
18 | 250 | mts | Supplying and providing 50 x 6mm GI strip for interconnection of earth electrodes pits including excavation. | 311 | 77750
19 |  |  | MV PANELS:
Fabrication, supply, erection, testing and commissioning of cubicle type, dust and vermin proof, floor mounted, front operated MV panel board made out of 14 SWG thick CRCA sheet, powder coated after 7 tank process, fully compartmentalised complete with hinges and earthed front doors with name plate, danger notice board, heavy duty rubber gaskets, removable gland plates made out of 3mm thick sheet steel with all necessary meters, indications, CTs etc as shown in the electrical drawing or as per the latest Electrical Inspectorate requirement complete with all connections and interconnections for the following panels.
Special Note: *All breaker releases shall be set as per the ratings shown in the drawings *Bus bar sizes shall be taken either as shown in the drawing or as design parameter of *0.8A/Sqmm for AL and 1.2A/Sqmm for Cu which ever is higher. *Cable Camber shall be provided for incoming & outgoing cables *Earth bus shall be full length of the panel and all Switches/breakers shall be earthed *GA drawings for all the panels before manufacturing shall submit to the Electrical Inspectorate/Consultant to get approval before manufacturing.
19.A |  |  | MSB
19.A | 1 | nos | Incomer: 1)1 no 630A 50kA 415V 50Hz,50kA, 4 Pole ACB set at 540A, wtih 1E/F and 3 O/C release and emergency trip switch. 2) 1 No. 200A 4pole 415V SDF Isolator. 3) 630A TPN busbar of best conductivity Aluminium (63.5 x 12.7Almm for Phase and 63.5 x 6.4mm for Neutral) with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoings: 1)1 No 250A 3P MCCB(Thermal Magnetic Type),35kA set at 185 A 2)2 No 200A 3P MCCB(Thermal Magnetic Type),35kA set at 160A 3)1 No 63A 3P MCCB(Thermal Magnetic Type),35kA set at 50A 4)2 No 160A 3P MCCB(Thermal Magnetic Type),35kA set at 100A 5)1 No 100A 3P MCCB(Thermal Magnetic Type),35kA set at 80A 6)1 No 400A 3P MCCB(Thermal Magnetic Type),35kA set at 315A | 505726 | 505726
Accessories 1)1 no mutifunction meters to read frequency, voltage and ampere having accuracy 0.5 with CT of 600/5A 15VA class-1 2) 1 no mutifunction meters to read frequency, voltage and ampere having accuracy 0.5 with CT of 200/5A 15VA class-1 3) 2 sets of RYB indicator lamps with apropriate fuses. 4) 1 No danger notice board of standard pattern.
The board shall be provided with 25 x 3mm copper earth bus for the full length. Painting letters / identifications for the incoming and outgoing switches, cable, fuse sizes, etc., in white enamel paint. The board shall be fabricated in such a way that future extension be possible. Accesories shall not be fitted on doors of switches/SDF/MCCBs(MSB).
19.B |  |  | SSB-1
| 1 | No | Incomer: 1) 1 no. 100A 35kA(Thermal Magnetic Type) 4P MCCB set at 80 A(as in scheme) 2) TPN busbar of best conductivity Aluminium of 25.4 x 6.4mm Al for Phase and 25.4 x 6.4mm Al for Neutral with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoings: 2 no. 40A 10kA 3P MCB, 2 no. 32A 10kA 3P MCB, 4 no. 25A 10kA 3P MCB, Accessories: 1 no danger notice board,fuse links, indication lamps 1 No (0-600V) voltmeter with selector switch (SSB-1) | 29315 | 29315
19.C |  |  | SSB-2
| 1 | No | Incoming: 1) 1 no. 160A 35kA 4P MCCB(Thermal Magnetic Type) set at 100A(as in scheme) 2) TPN busbar of best conductivity Aluminium of 25.4 x 9.5mm Al for Phase and 25.4 x 6.4mm Al for Neutral with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoing: 7 no. 25A 10kA 3P MCB, 1 no 63A 3P MCB Accessories: 1 no danger notice board,fuse links, indication lamps 1 No (0-600V) voltmeter with selector switch (SSB-2) | 34732 | 34732
19.D |  |  | SSB-4
Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required
| 1 | No | 3ph W double cover TPN vertical DB with provision for fixing 4pole MCCB as incomer and SP/TP MCB as outgoings
| 1 | No | Incoming: 1) 1 no. 63A 16kA 4P MCCB set at 50A(as in scheme) Outgoing: 4 no. 32 10kA TP MCB, Accessories: 1 no danger notice board | 18927 | 18927
20 |  |  | Supply & laying of one number PVC insulated and PVC sheathed armoured aluminium power cable of 1.1KV grade of the following sizes in ground including excavation of trench of size 35 x 75 cm, refilling the trench etc. as required but excluding sand cushioning and protective covering (in ordinary soil).
21 |  | mts | _Do- 3.5x 300 sqmm | UR
22 |  | mts | _Do- 3.5x 185 sqmm | UR
23 | 50 | mts | _Do- 3.5x 150 sqmm | 899 | 44950
24 | 50 | mts | _Do- 3.5x 95 sqmm | 623 | 31150
25 | 50 | mts | _Do- 3.5x 70 sqmm | 544 | 27200
26 |  | mts | _Do- 3.5x 50 sqmm | UR
27 |  | mts | _Do- 3.5x 35 sqmm | UR
28 |  | mts | Supply and laying 1runs of following sizes XLPE insulated armoured power cable of best conductivity Aluminium, 1.1KV grade conforming to IS 1554 using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages, colour washing etc. as required.
29 |  | mts | _Do- 3.5x 300 sqmm | UR
30 |  | mts | _Do- 3.5x 185 sqmm | UR
31 | 150 | mts | _Do- 3.5x 150 sqmm | 889 | 133350
32 | 100 | mts | _Do- 3.5x 95 sqmm | 600 | 60000
33 | 300 | mts | _Do- 3.5x 70 sqmm | 502 | 150600
34 |  | mts | do-3.5 x 50 sqmm-do- | UR
35 |  | mts | do- 4 x 16 sqmm -do- | UR
36 |  | mts | do- 4 x 10sqmm -do- | UR
37 |  | mts | do- 4 x 6 sqmm -do- | UR
38 | 6 | nos | Supply and providing end and core termination for 3.5 x 400sqmm cable including cost of gland, cable socket, earth etc including crimping etc | 3315 | 19890
39 | 2 | nos | _Do- 3.5x 150 sqmm | 1272 | 2544
40 | 2 | nos | _Do- 3.5x 95 sqmm | 931 | 1862
41 | 2 | nos | _Do- 3.5x 70 sqmm | 829 | 1658
42 |  | nos | _Do- 3.5x 50 sqmm | UR
43 | 20 | nos | Supply and providing cable route marker in cement concrete 1:2:4 with 10 cm x 10cm GI plate .5 mm thick with transcriptions bolted and welded to 35 x 35 x 6 mm angle | 207 | 4140
44 | 500 | nos | Painting letters or figures of 2.5cm/4cm/5cm height (Block, Roman, Italic, Indian) with white enamel paint as identifications marks to SSB, DBs, cables, switch boxes, etc., | 2 | 1000
45 | 1200 | kg | Supply, fabrication and erection of cable tray supports made of angle iron / flat iron including welding, painting, fixing, etc., | 110 | 132000
46 | 13 | nos | Supply and fixing of dry chemical powder type fire extinguishers of 5kg (ABC type) | 2324 | 30212
47 | 1 | set | supply and delivery at site of 4Nos fire buckets on one stand. The buckets shall be of round bottom, painted with red and marked “FIRE” in English and “ FIRE” in Malayalam. | 624 | 624
48 | 1 | mts | Supply and fixing artificial resuscitation chart in glass frame in Malayalam and in English | 204 | 204
49 | 4 | sq m | Supply and providing 2.5mm thick Elastomeric fire retardent insulating mat as per IS 15652/2006 to withstand 11 KV dielectric strength. | 2261 | 9044
50 | 2 | nos | Supply of 11KV grade rubber gloves | 300 | 600
51 | 1 | nos | Providing and fixing HT danger notice plate of size 200mmx150mm made of MS sheet steel at least 2mm thick and vitreous enamelled white on both sides and inscription in single red colour on front side as required | 140 | 140
52 | 50 | mts | Supply and laying Class 'B' GI pipe of 75mm dia with required accessories in ground including excavation of trench of size 1M x 30cm, refilling the trench, etc., as required as protective covering for cable at road crossing / vehicle traffic places. | 473 | 23650
53 | 50 | kg | Supply and providing MS chequered plate of suitable thickness including cutting, welding, painting etc. as required for the cable trench covering. | 63 | 3150
54 |  |  | PART4 GENERATOR
| 1 | no | Supply of 125KVA DG Set comprising Kirloskar /Greaves/Cummins/Mahindra diesel engine developing minimum 111 BHP coupled to Kirloskar /KEL / ELGI/Stamford make Alternator complete with standard control panel, fuel tank of suitable capacity and battery with leads and 6 nos anti-vibration pads and residential type silencer. Engine :- Kirloskar/Greaves/Cummins/Mahindra make 125 KVA / water cooled 4 stroke vertical 4 cylinder, in line type arrangement developing minimum 172.5 BHP at 1500 rpm diesel engine with 12/24 volt electric start and shut down system having high water temperature and low lube oil temperature. Alternator:- Kirloskar / KEL / ELGI/Stamford make alternator rated at 125KVA 3 phase 415 Volt 50 c/s 1500 rpm. Under normal conditions the voltage regulation will be +/- 5%. The alternator shall be of class"F" insulation and designed and built to withstand tropical conditions. | 750000 | 750000
Base frame:- Sturdy channel iron base frame welded construction for mounting engine and alternator. Control panel:- Wall / floor mounted totally enclosed sheet metal control panel, comprising 1 No 200A four pole MCCB set at 175A, 1 No AC Voltmeter (0-600V) with selector switch, 3 nos 600A Ammeter, 2 sets of indicator lamps, 1 No Frequency meter, 1 No KWH meter. The control panel shall be complete with necessary internal cables fuses and accessories as per Electrical Inspectorate standards . The erection of D.G. set also includes mechanical erection with anti-vibration pads, exhaust pipe, industrial silencer pipe, respective thermal insulation with mineral wool and Aluminium cladding.DG Set should be with acoustic chamber as per CPCB norm
| 1 | no | Unloading charges of 125 KVA DG set at site | 5500 | 5500
| 1 | no | Mechanical Installation, testing and commissioning of 125 KVA Diesel generator available at site complete with all necessary accessories | 15000 | 15000
| 1 | no | SITC of Insulating silencer with mineral /glass wool and aluminium cladding | 7500 | 7500
| 10 | mtrs | Exhaust piping complete with thermal insulation with mineral wool and cladding.MS pipe of suitable dia, heavy duty bend ,flexible connector and supports. | 2500 | 25000
| 1 | no | Supply, installation, testing and commissioning of freestanding indoor cubicle type 150 KVAR automatic power factor correction panel with 320A 3P 35kA MCCB incomer , APP capacitor (sprague) with BELUKE relay in 8 stages 25 KVAR x 4no, 20KVAR x 1 no,15 KVAR x 1 no ,10 KVAR x 1no,5KVAR x 1no with all accessories as in drawing etc complete as required for the installation.The panel shall be fabricated from a CPRI approved vendor and comply with CPRI standards. | 310000 | 310000
60 | 1 | Job | Preparation of all drawings ,Sumitting and getting approval from electrical inspectorate, arrange inspection, getting sanction and energisation certificate from electrical inspectorate and KSEB,obtaining power allocation and our connection etc. for commissioning of the whole installation. | 30000 | 30000
|  |  | Sub Total |  | 4031291
62 | 1 | Job | KSEB Charges including cost of RMU etc. | 950000 | 950000
|  |  | Grand Total |  | 4981291
(Rupees forty nine lakh eighty one thousand two hundred and ninety one only)