## Sheet1
Estimate for the Electrification of Engineering College, Pathanapuram, Pathanamthitta (Electrical Block)
LT Electrification
Item No | Qty | Unit | Specification of Items | Rate in rupees | Amount in Rupess
1 |  |  | Supply and wiring points according to IS 732-1989 in existing PVC conduit of minimum size 20 mm with specials conforming to IS 9537 part III 1983 and with suitable size specials conforming to IS 3419-1988, fixing the conduit using metal saddles spacing not exceeding 50 cm or concealed suitably and with 1.00 sq mm PVC insulated stranded single core copper conductor cable 650V grade, and continuous earthing with1.5 sq mm green coloured FR PVC insulated copper conductor cable , required qty of copper earth socket, brass bolt and nut crimping/ soldering etc complete with suitable size modular type metal switch boxes, modular type front plates (white or off white) etc. up to and including 6 A modular type SP switches and making good the surface of wall, colour washing etc. complete. All the terminations in the switch boards and DB's shall be tinned and the wires shall be drawn and fixed along the periphery of the box using suitable ties, tie mounts etc as required. (Group B modular accessories)
a | 298 | Each | Single control light point with 6A, 3 plate ceiling rose | 676 | 201448
b | 6 | Each | Twin control light point with 6A, 3 plate ceiling rose | 1014 | 6084
c | 107 | Each | Single control light point without ceiling rose | 657 | 70299
d |  | Each | Twin control light point without ceiling rose | UR
e | 107 | Each | Single control ceiling fan point with 6 A, 3 plate ceiling rose & with socket size stepped electronic regulator. | 1309 | 140063
f | 1 | Each | Call bell point with piano type 6 A bell push at one end and 6 A, 3 plate ceiling rose at other end | 714 | 714
g | 30 | Each | Combined plug point with 6 A, 5 pin plug socket controlled by 6 A switch in the same switch board as that of light points. | 338 | 10140
h |  | Each | Supply and wiring 6A 3 pin sockets controlled by 6A SP switch in independent position. | UR
i | 1 | Each | Supply and fixing RJ 11 twin telephone sockets | 405 | 405
2 | 104 | Each | Supply and installation of suitable size MS rod type fan clamp as per IS 732 as required. | 124 | 12896
3 | 3 | Each | Supply and installation of suitable size MS belt type fan clamp fabricated from MS flat (2 pieces) as per IS 732 as required. | 182 | 546
4 | 107 | Each | Supply, conveyance, installation, testing and commissioning of ceiling fans of 1200mm sweep (5 star rated) using standard accessories excluding resistance type regulator, wiring the down rod with 16/0.20mm PVC insulated and PVC sheathed 650/1100V grade 3 core round copper conductor flex wire or with extended original wiring etc. as required. | 1853 | 198271
5 | 75 | mtr | Supply and providing every additional length of down rod of suitable size heavy gauge GI / WI pipe with 16/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming in relevant ISS or with original wiring extended including painting as required. | 115 | 8625
6 | 293 | Each | Conveyance, installation, testing and commissioning of pre-wired fluorescent light fittings with all accessories and fluorescent lamps of all types directly on wall and giving connections with 16/0.20 mm 3 core PVC insulated and sheathed round copper conductor flex wire or extending the original wiring and giving connections as required | 138 | 40434
7 | 5 | Each | Conveyance, installation, testing and commissioning of pre-wired fluorescent fittings of all types complete with all accessories and fluorescent lamps etc. including supplying and fixing ball and socket arrangements on T.W round block, suspension down rod of 19 mm dia MS conduit up to 2x30cm length including painting and wiring the down rod with 16/0.20mm 3 core round copper conductor flex wire conforming to relevant ISS or extending the original wiring and giving connections etc. a required. | 371 | 1855
8 | 3 | mtr | Supplying and providing extra H.G conduit down rod of 19 mm dia 2 x 1.00 m long with 16/0.20 mm 3 core copper conductor flex wire conforming to relevant ISS or with the extended original wiring and giving connection etc. as required. | 198 | 594
9 | 89 | Each | Supply and fixing angle / straight brass lined skirt type, bakelite batten holder without shade and giving connection etc as required | 63 | 5607
10 | 4 | Each | Conveyance, installation, testing and commissioning of ornamental type wall light fittings of all types directly on wall including giving connections with required length of 16/0.20 mm 3 core round copper conductor flex wire conforming to relevant ISS or with the extended original wiring, making good the damages, colour washing etc as required | 67 | 268
11 | 119 | Each | Supply and fixing 11W CFL lamp in the existing holder | 156 | 18564
12 | 30 | Each | Supply and fixing cast aluminium stove enameled bulk head fitting with deep drawn anodised aluminium body, epoxy powder coated, heat resistant prismatic glass cover suitable for 9 W CFL to wall / ceiling including giving connections with required length of 16/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming to relevant ISS or extending the original wiring and making good the surface as required. | 601 | 18030
13 | 45 | Each | Supply and fixing 6/16A shuttered socket with16A control switch modular type in company made box and front plate.(Group B) | 665 | 29925
14 |  |  | Supply and laying medium gauge PVC conduit conforming to IS 9537/1983 Part III n roof slab, jointing the pipes with PVC solvent cement, tying & fixing the conduit firmly with the re-inforcement etc. as required. |  | 0
a | 1830 | mtr | 20 mm | 41 | 75030
b | 610 | mtr | 25 mm | 49 | 29890
15 |  |  | Supply and fixing the following deep PVC accessories conforming to IS 3419/1988 along with the PVC conduits laid in concrete |  | 0
a | 162 | Each | 20 mm 1 way deep junction box | 50 | 8100
b | 95 | Each | 20 mm two way through junction box | 51 | 4845
c | 65 | Each | 20 mm 3 way angle junction box | 52 | 3380
d | 115 | Each | 20 mm 4 way angle junction box | 55 | 6325
e | 5 | Each | 25 mm 1 way deep junction box | 53 | 265
f | 5 | Each | 25 mm two way through junction box | 56 | 280
g | 5 | Each | 25 mm 3 way angle junction box | 58 | 290
h | 5 | Each | 25 mm 4 way angle junction box | 61 | 305
16 |  |  | Supply and fixing the following sizes of medium guage PVC Conduit conforming to IS 9537 / 1983 part III along with all required accessories in recess including cutting the wall and making good the damages etc as required. |  | 0
a | 800 | mtr | 20mm | 124 | 99200
b | 360 | mtr | 25mm | 136 | 48960
17 |  |  | Supply and drawing 650/1100 V grade PVC insulated stranded single core copper conductor cables conforming to IS 694 part I 1990 in the existing surface / recess conduit as required including giving necessary connections of the following sizes. |  | 0
a | 2500 | mtr | 1.5sq mm 3 run( R/Y/B/Black/Green) | 77 | 192500
b | 1300 | mtr | 1.5sq mm single run( green) | 45 | 58500
c | 1300 | mtr | 2.5sq mm 2 run | 81 | 105300
d |  | mtr | 4sq mm 2 run | 106 | 0
e | 100 | mtr | 4sq mm 4 run | 184 | 18400
f | 100 | mtr | 6sq mm 4 run | 260 | 26000
18 | 50 | mtr | Supply and drawing No.14 SWG copper along with 4sq.mm mains | 26 | 1300
19 | 400 | mtr | Supply and drawing No.10 SWG copper along wiring | 62 | 24800
20 | 10 | nos | Supply and providing superior quality copper earth socket suitable for No.14 SWG copper and Crimping | 18 | 180
21 | 60 | nos | -Do- No.10 -Do - | 19 | 1140
22 | 0.5 | mtr | Supplying and clamping 25 x 3 mm tinned Copper strip on wall | 152 | 76
23 |  |  | Supply, laying and clamping of 1 no.XLPE insulated and PVC sheathed armoured aluminium power cable, 1.1 KV grade of the following sizes using clamps noted along with the cables, spacing of clamps not exceeding 60cms, making good the damages , colour washing etc. as required. |  | 0
a | 70 | mtr | 3.5Cx240 sq mm | 1330 | 93100
b | 45 | mtr | 3.5Cx150 sq mm | 889 | 40005
c | 19 | mtr | 3.5Cx70 sq mm | 502 | 9538
d | 20 | mtr | 3.5Cx25 sq mm | 271 | 5420
e | 23 | mtr | 4Cx16 sq mm | 231 | 5313
24 |  |  | Supplying siemens / tropodur type nickel plated single compression brass cable gland for PVC insulated and PVC sheathed armoured aluminium/ copper conductor cable 1.1 KV grade, and making end termination suitable for 2/ 3/ 3½/ 4 core cable of the following sizes as required. |  | 0
a | 2 | nos | 3.5Cx240 sq mm | 1377 | 2754
b | 2 | nos | 3.5Cx150 sq mm | 1008 | 2016
c | 6 | nos | 3.5Cx70 sq mm | 714 | 4284
d | 2 | nos | 3.5Cx25 sq mm | 474 | 948
e | 4 | nos | 4Cx16 sq mm | 319 | 1276
25 |  |  | Supplying and providing earth clamps for siemens/ tropodur type cable glands of suitable length and other dimensions noted along with each size of glands for the following sizes of cables as required. |  | 0
a | 2 | nos | 240 sq mm | 142 | 284
b | 2 | nos | 150 sq mm | 99 | 198
c | 6 | nos | 70 sq mm | 27 | 162
d | 2 | nos | 25 sq mm | 27 | 54
e | 4 | nos | 16 sq mm | 18 | 72
26 |  |  | Supply of superior quality aluminium tubular cable socket and making core termination of cables of the following sizes including crimping etc. as required. |  | 0
a | 3 | nos | 240 sq mm | 77 | 231
b | 3 | nos | 150 sq mm | 47 | 141
c | 1 | nos | 120 sq mm | 42 | 42
d | 1 | nos | 95 sq mm | 26 | 26
e | 3 | nos | 70 sq mm | 24 | 72
f | 1 | nos | 35 sq mm | 16 | 16
g | 3 | nos | 25 sq mm | 14.4 | 43.2
h | 5 | nos | 16 sq mm | 13.7 | 68.5
27 |  |  | Supply and installation of sheet steel, phosphatised and painted, dust and vermin proof enclosure of MCB DB including copper /brass bus bar, neutral link, earth bus and DIN rail suitable for fixing MCB/ isolator etc. fixed on wall using suitable anchor bolts or fixed in recess including cutting hole on the wall , making good the damages, colour washing etc. as required |  | 0
a | 1 | nos | 4P enclosure for independent mounting of MCB | 604 | 604
b | 1 | nos | 4 way (8+12) - double cover TPN vertical DB with provision for fixing 4P MCB / Isolator/ RCCB/ RCBO as incomer and SP/ TP MCB as outgoing (IP 42/43) | 7739 | 7739
c | 2 | nos | 6 way (8+18) - double cover TPN vertical DB with provision for fixing 4P MCB / Isolator/ RCCB/ RCBO as incomer and SP/ TP MCB as outgoing (IP 42/43) | 8960 | 17920
d | 4 | nos | 4 way (8+12) - three phase double cover (IP 42/43) | 3329 | 13316
e | 3 | nos | 6 way (8+18) - three phase double cover (IP 42/43) | 4039 | 12117
f | 2 | nos | 8 way (8+24) - three phase double cover (IP 42/43) | 4783 | 9566
28 |  |  | Supply and installation of the following accessories suitable for 50 Hz , AC supply conforming to IS 8828-1995/ IEC 60898 of the following current ratings in the existing enclosure and giving connections as required |  | 0
b | 1 | nos | S&F 100A 4P Minibreak Isolator | 1246 | 1246
c | 3 | nos | S&F 63A 4P Minibreak Isolator | 752 | 2256
d | 4 | nos | S&F 40A 4P Minibreak Isolator | 716 | 2864
e | 5 | nos | S&F 32A 4P Minibreak Isolator | 668 | 3340
f | 4 | nos | Supply and fixing 40A 30mA FP RCCB | 2780 | 11120
g | 5 | nos | Supply and fixing 25A 30mA FP RCCB | 2744 | 13720
h | 8 | nos | Supplying and fixing 25A TP MCB 10kA | 919 | 7352
i | 8 | nos | Supplying and fixing 40A TP MCB 10kA | 1369 | 10952
j | 49 | nos | Supplying and fixing 16A SP MCB 10kA | 219 | 10731
k | 101 | nos | Supplying and fixing 6A SP MCB 10kA | 219 | 22119
l | 2 | nos | Supply and istallation of cable box for 3 ph 6W DB | 832 | 1664
m | 1 | nos | Supply and istallation of cable box for 3 ph 4W DB | 808 | 808
29 |  |  | Cost of Fluorescent tube light fitting with lamp holder, APF electronic ballast suitable for continuous operation with THD <10%, power factor >0.98, RoHS compliant,high lumen tube, duly wired up for use on 230 V AC supply . The fittings shall be made from CRCA MS sheet of minimum thickness 0.50 mm nominal thickness inside & outside. |  | 0
a | 247 | nos | Suitable for single 28W T5 lamp | 1322 | 326534
30 | 21 | Each | Supply, conveyance, installation, testing and commissioning of the 300/305mm, single phase light duty exhaust fan with metal framein the existing opening, fixing necessary bolt and nuts, making good the damages etc. as required including giving connections with required length of 24/0.20mm PVC insulated and PVC sheathed 3 core round copper conductor flex wire conforming to relevant ISS. | 1828 | 38388
31 |  |  | MV PANELS:
Fabrication, supply, erection, testing and commissioning of cubicle type, dust and vermin proof, floor mounted, front operated MV panel board made out of 14 SWG thick CRCA sheet, powder coated after 7 tank process, fully compartmentalised complete with hinges and earthed front doors with name plate, danger notice board, heavy duty rubber gaskets, removable gland plates made out of 3mm thick sheet steel with all necessary meters, indications, CTs etc as shown in the electrical drawing or as per the latest Electrical Inspectorate requirement complete with all connections and interconnections for the following panels.
Special Note: *All breaker releases shall be set as per the ratings shown in the drawings *Bus bar sizes shall be taken either as shown in the drawing or as design parameter of *0.8A/Sqmm for AL and 1.2A/Sqmm for Cu which ever is higher. *Cable Camber shall be provided for incoming & outgoing cables *Earth bus shall be full length of the panel and all Switches/breakers shall be earthed *GA drawings for all the panels before manufacturing shall submit to the Electrical Inspectorate/Consultant to get approval before manufacturing.
a |  |  | SB-Electrical Block
| 1 | No | Incoming: 1) 1 no. 250A 36kA 4P MCCB(Thermal Magnetic Type) set at 200A(as in scheme) 2) TPN busbar of best conductivity Aluminium of 31.8 x 9.5mm Al for Phase and 31.8 x 6.4mm Al for Neutral with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoing: 63A 25kA 3P MCCB set at 50A-1 nos 63A 25kA 3P MCCB set at 40A-2 nos 125A 25kA 3P MCCB set at 100A-2 nos 160A 25kA 3P MCCB set at 150A-1 nos Accessories: 1 no danger notice board,fuse links, indication lamps 1 No (0-600V) voltmeter with selector switch | 99010 | 99010
b |  |  | SB-LAB
| 1 | No | Incoming: 1) 1 no. 160A 25kA 4P MCCB(Thermal Magnetic Type) set at 150A(as in scheme) 2) TPN busbar of best conductivity Aluminium of 25.4 x 9.5mm Al for Phase and 25.4 x 6.4mm Al for Neutral with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoing: 125A 16kA 3P MCCB set at 100A-6 nos Accessories: 1 no danger notice board,fuse links, indication lamps 1 No (0-600V) voltmeter with selector switch | 82400 | 82400
c |  |  | SB-DC
| 1 | No | Incoming: 1) 1 no. 160A DP isolator(as in scheme) 2) DP busbar of best conductivity Aluminium of 25.4 x 9.5mm Al for Phase and for Neutral with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoing: 25A 250V DC DP MCB-10 nos Accessories: 1 no danger notice board | 18441 | 18441
d |  |  | SB-AC1
| 1 | No | Incoming: 1) 1 no. 100A 4P isolator(as in scheme) 2) TPN busbar of best conductivity Aluminium of 25.4 x 6.4mm Al for Phase and 25.4 x 6.4mm Al for Neutral with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoing: 25A 415V FP MCB-10 nos Accessories: 1 no danger notice board,fuse links, indication lamps | 20740 | 20740
e |  |  | SB-AC2
| 1 | No | Incoming: 1) 1 no. 100A 4P isolator(as in scheme) 2) TPN busbar of best conductivity Aluminium of 25.4 x 6.4mm Al for Phase and 25.4 x 6.4mm Al for Neutral with heat shrinkable sleeves mounted on DMC/FRP busbar supports with extensible busbar Outgoing: 25A 415V FP MCB-10 nos Accessories: 1 no danger notice board,fuse links, indication lamps | 20740 | 20740
32 | 2 | nos | Supply and providing plate earthing as per IS 3043 with 1200x1200x12 mm GI/CI earth plate, 50 mm GI watering pipe fixed to the earth plate with 25 x 3mm GI clamps, GI funnel with weld mesh, filling required quantity of charcoal including construction of inspection chamber with a bed concrete of 1:4:8 PCC using 40 mm broken stone (10 cm thick), brick work in cement mortar 1:6, plastering the surface of brick masonry and the exposed surface of PCC bed with cement mortar 1:4, 12 mm thick, (the finished inside dimension shall be 450 x 450 x 450 mm) but excluding test joint, earth continuity conductor to the plate, and covering at the top. (in ordinary soil) | 10652 | 21304
33 |  |  | Supply and providing test joint for the earthing system using 2 Nos of the following sizes of strips including cutting and bending to shape, drilling necessary holes and fixed to the watering pipe etc as required. |  | 0
a | 2 | nos | 2x40x3mm GI strip | 215 | 430
34 |  | nos | Supply and providing the following sizes of cast iron gully trap with covering at the top of the inspection chamber of earth pit as required |  | 0
a | 2 | nos | 450x450x10mm | 929 | 1858
35 | 5 | mts | Supplying and connecting 25x6 GI strip from test joint to plate | 242 | 1210
36 | 50 | kg | Supplying and installation including all manner of supports/ suspenders, anchor bolts etc for cable trays made out of suitable size channel sections, slotted angles, flats, MS plates etc as required including painting with 2 coats of synthetic enamel paint over a coat of zinc chromate primer, making good the damages, colour washing etc as required. | 110 | 5500
37 |  | kg | Supplying and installation of supports, anchor bolts etc made out of suitable size single section MS angle, flats etc as required including painting with 2 coats of synthetic enamel paint | UR
Total |  |  |  |  | 2421886.7
(Twenty four lakh twenty one thousand eight hundred and eighty seven only)